## Standard Permit GRA1
Generic risk assessment for draft standard rules set number SR2022 No01 v1.0
Standard Facility: |  |  |  | Part A installation. On-farm AD including the use of the resultant biogas.
Location: |  |  |  | Applies to all potential locations.
Risk assessment carried out by: |  |  |  | Natural Resources Wales
Date: |  |  |  | 27th March 2023
The scope of the permit and associated rules is defined by the following risk criteria:
| Parameter 1 | Permitted activities - The storage and recovery of waste (R1, R3, R13) and combustion of biogas (D10).
| Parameter 2 | Permitted wastes - manures and slurries, biodegradable wastes arising on-farm and dairy wastes suitable for digestion.
| Parameter 3 | Except for the auxiliary flare, the aggregate rated thermal input of all appliances used to burn biogas must be less than 5 megawatts.
| Parameter 4 | Maximum quantity of waste - including solids and liquids - shall be limited to 100,000 tonnes per year and with the capacity to treat more than 100 tonnes per day.
| Parameter 5 | No point source discharges to controlled waters or groundwater.
| Parameter 6 | The activities shall not be carried out within 500 metres of a European site or Site of Special Scientific Interest (excluding those designated solely for geological features).
| Parameter 7 | Gas engines stacks must be 7 metres or more in height or have an effective stack height of 3 metres or more.
| Parameter 8 | The gas engine stack(s) must not within 200 metres of the nearest sensitive receptor.
| Parameter 9 | The activities must not be carried out within an Air Quality Management Area (AQMA).
| Parameter 10 | The activitiies cannot be within a groundwater source protection zone 1, or if a source protection zone has not been defined then within 50 metres of any well, spring or borehole used for the supply of water for human consumption. This must include private water supplies.
| Parameter 11 | The activities must not be carried out within 10 metres of any watercourse
Data and information |  |  |  |  | Judgement |  |  | Action (by permitting)
Receptor | Source | Harm | Pathway | Probability of exposure | Consequence | Magnitude of risk | Justification for magnitude | Risk management | Residual risk
What is at risk? What do I wish to protect? | What is the agent or process with potential to cause harm? | What are the harmful consequences if things go wrong? | How might the receptor come into contact with the source? | How likely is this contact? | How severe will the consequences be if this occurs? | What is the overall magnitude of the risk? | On what did I base my judgement? | How can I best manage the risk to reduce the magnitude? | What is the magnitude of the risk after management? (This residual risk will be controlled by Compliance Assessment).
Local human population. | Releases of oxides of nitrogen (NO2), carbon monoxide (CO), sulphur dioxide (SO2), total volitile organic compounds (VOCs). | Harm to human health - respiratory irritation and illness. | Air transport then inhalation. | Low | Medium | Medium | There is potential for exposure to anyone living close to the site or at locations where members of the public might be regularly exposed. | Activities shall be managed and operated in accordance with a management system (will include inspection and maintenance of equipment, including engine management systems), point source emissions to air with associated emission limits and monitoring. | Low
Local human population | Release of unburnt biogas | Harm to human health - respiratory irritation and illness. Release of potent climate change gases. | Air transport | Medium | High | Medium | Potential for release in emergency and maintenance via pressure relief valves | Auxiliary flare are available and used but limited to emergency situation and planned miantance. Pressure relief valves are inspected regularly. Unplanned releases are reported. | Low
Local human population. | Release of microorganisms (bioaerosols). | Harm to human health - respiratory irritation and illness. | Air transport then inhalation. | Medium | High | Medium | Potential for release at waste reception/treatment and maturation. | Maturation activities are not carried out in the open within 250m metres of the nearest sensitive receptor. Operations have to take place within a closed system with appropriate filters or scrubbing system. | Low
Local human population | Odour | Nuisance, loss of amenity | Air transport then inhalation. | Medium | Medium | Medium | Local residents often sensitive to odour. Waste types/odours are typical to those already used on agricultural premises. | Emissions shall be free from odorous compounds. An odour management plan is required. Non- point source emissions of biogas shall be minimised using appropriate measures. All storage tanks and lagoons are required to be covered also AD is an enclosed process. A buffer zone for odour has been kept at 200 metres from the nearest sensitive receiver so that below this limit odour control can be assessed in a bespoke permit. | Low
Local human population. | Noise and vibration. | Nuisance, loss of amenity, loss of sleep. | Noise through the air and vibration through the ground. | Low | Low | Low | Local residents often sensitive to noise and vibration but there is low potential for exposure. | Noise and vibration shall be minimised and not cause nuisance. A noise and vibration management plan may be required. | Low
Local human population and / or livestock after gaining unauthorised access to the installation. | All on-site hazards: machinery. | Bodily injury. | Direct physical contact. | Low | Medium | Low | Direct physical contact is minimised by activity being carried out within enclosed digesters so a low magnitude risk is estimated. | Activities shall be managed and operated in accordance with a management system (will include site security measures to prevent unauthorised access). | Low
Local human population and local environment. | Arson and / or vandalism causing the release of polluting materials to air (smoke or fumes), water or land. | Respiratory irritation, illness and nuisance to local population. Injury to staff, fire fighters or arsonists/vandals. Pollution of water or land. | Air transport of smoke. Spillages and contaminated firewater by direct run-off from site and via surface water drains and ditches. | Medium | High | Medium | Although biogas is flammable, risk of direct physical contact is reduced by activity being carried out within enclosed systems. | As above. An accident management plan is required as part of management system (will include fire and spillages). | Low
Local human population and local environment. | Accidental explosion and fire causing the release of polluting materials to air (smoke or fumes), water or land. | Respiratory irritation, illness and nuisance to local population. Injury to staff, fire fighters or arsonists/vandals. Pollution of water or land. | Air transport. Spillages and digestate direct run-off from site and via surface water drains and ditches. | Low | High | Medium | Unlikely to happen - reduced by effective management systems. | Management systems required to include DSEAR assessment. Bunding of tanks or method of retaining and recovering any loss etc. | Low
Local human population and local environment. | Accidental fire causing the release of polluting materials to air (smoke or fumes), water or land. | Respiratory irritation, illness and nuisance to local population. Injury to staff or fire fighters. Pollution of water or land. | As above. | Low | Medium | Medium | Risk of accidental combustion of waste is moderate. | As above | Low
All surface waters close to and downstream of site. | Spillage of liquids, including oil. | Acute effects: fish kill. | Direct run-off from site across ground surface, via surface water drains, ditches etc. | Low | Medium | Low | Potential for spillage from digestions tanks and storage vessels. | Digestion tanks built to appropriate standard. No point source emissions to water. Run off restricted to clean surface water using appropriate measures. All biogas condensate shall be discharged into a sealed drainage system. Impermeable surface required for storage of all wastes. | Low
All surface waters close to and downstream of site. | As above | Chronic effects: deterioration of water quality. | As above. Indirect run-off via the soil layer. | Low | Medium | Low | As above | As above | Low
Abstraction from watercourse downstream of facility (for agricultural or potable use). | As above | Acute effects, closure of abstraction intakes. | Direct run-off from site across ground surface, via surface water drains, ditches etc. then abstraction. | Low | Medium | Low | Watercourse must have medium / high flow for abstraction to be permitted, which will dilute contaminated run-off. | As above | Low
Groundwater | As above | Chronic effects: contamination of groundwater, requiring treatment of water or closure of borehole. | Transport through soil/groundwater then extraction at borehole. | Low | Medium | Low | Potential for spillage from digestions tanks and storage vessels. | As above. Activities cannot take place within groundwater protection zone 1 or if a source protection zone has not been defined then within 50 metres of any well, spring or borehole used for the supply of water for human consumption. This must include private water supplies. Impermeable surface required for AD plant. | Low
Protected nature conservation sites - European sites and SSSIs. | Any, but principally NOx. | Harm to protected site through toxic contamination, nutrient enrichment, disturbance etc. | Any | Low | Medium | Low | Emissions to air may cause harm to and deterioration of nature conservation sites. | Emissions of substances not controlled by emission limits (excluding odour and noise) shall not cause pollution. The operator shall not be taken to have breached this rule if appropriate measures, including, but not limited to, those specified in any approved emissions management plan, have been taken to prevent or where that is not practicable, to minimise, those emissions. At 500 metres or above, the potential hazards from the permitted activities pose a low risk to the broad sensitivity of species and habitats groups. The standard permit only applies at this distance or more. Emission limits for stack gases are specified. | Low
Notes: | Red triangle indicates comment containing supporting information
Yellow columns contain drop down menus that allow automatic evaluation of risk in green column
| Very low | Low | Medium | High
High | 4 | 8 | 12 | 16
Medium | 3 | 6 | 9 | 12
Low | 2 | 4 | 6 | 8
Very low | 1 | 2 | 3 | 4
|  |  |  | Very low |  | #REF! | #REF! | #REF! | #REF!
|  |  |  | Low |  | 2 | 3 | 6 | Medium
|  |  |  | Medium |  | #REF! | #REF! | #REF! | #REF!
|  |  |  | High |  | 2 | 3 | 6 | Medium
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | 3 | 3 | 9 | Medium
| Very low | Low | Medium | High |  | #REF! | #REF! | #REF! | #REF!
Very low | 1 | 2 | 3 | 4 |  | #REF! | #REF! | #REF! | #REF!
Low | 2 | 4 | 6 | 8 |  | #REF! | #REF! | #REF! | #REF!
Medium | 3 | 6 | 9 | 12 |  | #REF! | #REF! | #REF! | #REF!
High | 4 | 8 | 12 | 16 |  | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
[6 empty] | #REF! | #REF! | #REF! | #REF!
Note on B27: Receptors to consider should include: atmosphere, land, surface waters, groundwater, humans, wildlife and their habitats. A single receptor may be at risk from several different sources and all must be addressed.
Note on C27: The Source of hazard will be the activity or operation taking place for which a particular hazard may arise.
Note on D27: Harm may arise when a specific hazard is realised.
Note on E27: Pathways are the routes or means by which defined hazards may potentially realise their consequences at the receptors.
Note on F27: Probability of exposure is the likelihood of the receptors being exposed to the hazard. Example definitions: High – exposure is probable: direct exposure likely with no / few barriers between hazard source and receptor; Medium – exposure is fairly probable: feasible exposure possible - barriers to exposure less controllable; Low – exposure is unlikely: several barriers exist between hazards source and receptors to mitigate against exposure: Very Low – exposure is very unlikely: effective, multiple barriers in place to mitigate against exposure.
Note on G27: The consequences of a hazard being realised may be actual or potential harm. This will include be on a high/medium/low/very low score using attributes and scaling to consider 'harm'.
Note on J27: Risk management involves breaking or limiting the source-pathway-receptor linkage to reduce risk.
Note on H27: Magnitude of the risk is determined by combining the probability with the magnitude of the potential consequences High risks require additional assessment and active management Medium risks require additional assessment and may require active management/monitoring Low and very low risks require periodic review.